## Slide 1: Industrial Control System Cyber Crime
Ukranian Power Grid Hack

## Slide 2: PowerGrid

## Slide 3: Background
For power to be useful in a home or business, it comes off the transmission grid and is stepped-down to the distribution grid
It often has circuit breakers and switches so that the substation can be disconnected from the transmission grid or separate distribution lines can be disconnected from the substation when necessary.
Ukraine has 24 regions, each divided between 11 and 27 provinces, with a different power distribution company serving each region.

## Slide 4: Introduction
It was 3:30 p.m. last December 23rd, Ivano-Frankivsk region of Western Ukraine, Prykarpattyaoblenergo control center, the cursor on one of the operator’s computer suddenly skittered across the screen of its own accord.
He watched as it navigated purposefully toward buttons controlling the circuit breakers at a substation in the region and then clicked on a box to open the breakers and take the substation offline.
A dialogue window popped up on screen asking to confirm the action, and the operator stared dumbfounded as the cursor glided to the box and clicked to affirm.

## Slide 5: Introduction
The operator grabbed his mouse and tried desperately to seize control of the cursor, but it was unresponsive.
All he could do was stare helplessly at his screen while the ghosts in the machine clicked open one breaker after another, eventually taking about 30 substations offline
The hacker also disabled backup power supplies to two of the three distribution centers, leaving operators themselves stumbling in the dark.

## Slide 6: Reconnaissance Phase
Getting into the Network
  Last Spring, the attackers delivered spear-phishing email with a malicious Word document attached targeting IT staff and system administrators working for multiple companies responsible for distributing electricity throughout Ukraine.
  When workers clicked on the attachment, a popup displayed asking them to enable macros for the document. If they complied, a program called BlackEnergy3 infected their machines and opened a backdoor to the hackers.
  The initial intrusion got the attackers only as far as the corporate networks. But they still had to get to the SCADA networks that controlled the grid.

## Slide 7: Reconnaissance Phase
Getting into SCADA
  Over many months of exploring and mapping the networks, they got access to the Windows Domain Controllers, where user accounts for networks are managed.
  They harvested worker credentials, some of them for VPNs the grid workers used to remotely log in to the SCADA network.

## Slide 8: Reconnaissance Phase
Reconfiguring the UPS
  They reconfigured the uninterruptible power supply, or UPS, responsible for providing backup power to two of the control centers.
Replacing legitimate firmware
  They wrote malicious firmware to replace the legitimate firmware on serial-to-Ethernet converters at more than a dozen substations resulting in blocking operators from sending remote commands to re-close breakers once a blackout occurred.

## Slide 9: Incident
Sometime around 3:30 p.m. on December 23 they entered the SCADA networks through the hijacked VPNs and sent commands to disable the UPS systems they had already reconfigured.
Then they began to open breakers.
They launched a telephone denial-of-service attack against customer call centers to prevent customers from calling in to report the outage.
As the attackers opened up breakers and took a string of substations off the grid, they used their malicious firmware to render the converters thereafter inoperable and unrecoverable, unable to receive commands.
After they had completed all of this, they then used a logic bomb that launched malware called KillDisk automatically about 90 minutes into the attack to wipe files from operator stations to render them inoperable as well.
This would have been around 5 p.m., the same time that Prykarpattyaoblenergo posted a note to its web site acknowledging for the power outage.
Half an hour later , the company then posted a second note to customers saying the cause of the outage was hackers.

## Slide 10: Aftermath
The power wasn’t out long in Ukraine: just one to six hours for all the areas hit, but 230000 people was affected
This is the first cyber attack that resulted in a blackout
But more than two months after the attack, the control centers are still not fully operational.
The power is on, but workers still have to control the breakers manually.

## Slide 11: What was Wrong and What can be done
The control systems in Ukraine were more secure than some in the US, since they were well-segmented from the control center business networks with robust firewalls.
    In the end they still weren’t secure enough—workers logging remotely into the SCADA network weren’t required to use two-factor authentication, which allowed the attackers to hijack their credentials and gain crucial access to systems that controlled the breakers.

## Slide 12: What was Wrong and What can be done
The employees did not have awareness about spear-phishing
The networks does not support constant monitoring protocols that recognize the anomalies which indicate potentially threatening behavior because "if a misconfiguration is made by accident, or malicious code is knocking at the door of a network, protection strategies of this kind can significantly reduce the risk of system outages through cyber attacks”.
  It should be common practice to train the employees about phishing and having white-listing technology in place, rather than just anti-virus software.

## Slide 13
Questions ?